EOCR-SSD

■; MCU( Microprocessor Control Unit ) Based/2-CT Type. ■; Real Time Processing/Higher Preceision. ■; Current Setting Range 05Type:0.5~6A/30Type:3~30A/60Type:10~60A. ■; Indicating real current on the display. ■; Trip cause digital display for easy trouble shooting. ■; Reset:Manual(instantaneous)/Electrical(remote). ■; Load selection by DIP switch:Single phase(1P)/Three phase(3P). ■; Fail-safe(N)/Non-Fail-safe(R)..

Protective Item; Trip Time; Descrption. Over-current; O-TIME; Is<In. Phase Loss; 3 sec; .. Locked Rotor; 0.5sec after elapse of dt; >2times OC setting value..

Over-Current Setting; Current; 05; 0.5 ~ 6A. 30; 3.0 ~ 30A. 60; 10 ~ 60A. Starting delay time; D-TIME; 1 ~30 sec. Trip time; O-TIME; 0.5, 1~10 sec. Operating t-c characteristic; Over-Current; Definite. Tolerance; Current; ±5%. TIME; ±5%. Environment; Temperature; Operation; -20 ~60℃. Store; -30 ~80℃. Humidity; 30~85% RH Non-condensing. Control Power; 220 : 220VAC±15%, 50/60Hz. 110 : 110VAC ±15%, 50/60Hz. Output relay; 2-SPST; 3A / 250VAC Resistive. Insulation; Between casing and circuit; Over 10MΩ, 500VDC. Dielectric Strenghth; Between casing and circuit; 2000VAC 60Hz, 1min. Between open contacts; 1000VAC 60Hz, 1min. between circuit; 2000VAC 60Hz, 1min. Reset; Manual/Electrical. Installation; 35mm DIN-Rail or Panel Munting..