| EOCR-3DE. EOCR-FDE.; ■; Compact Design. ■; MCU( Microprocessor Control Unit ) Based. ■; Three Integral Current Transformers. ■; Multiple Protection Functions. ■; Digital Ammeter/3 Phase Current Display. ■; Troubleshooting/Trip Cause Memory, Display. ■; Adjustable Operating Features by Mode switch. ■; Wide Current Adjustment Range. ■; Selectable Time-Current Characteristics(Inverse/Definite). ■; Manual(Instantaneous)/Electrical(Remote)Reset. ■; Test Function. ■; Ambient Insensitive. ■; Selectable Fail-safe and Non-fail-safe Operation Modes. ■; Inverter (20~400Hz). ■; EOCR-3DE : Panel Mounting type. ■; EOCR-FDE : Flush Mounting type(Display).. |
| --- |
| Protective Item; Trip Time. Over-current; DEF : 0.2~30sec INV : 1~30. Undercurrent; 0.5~30 sec. Phase Loss; within 3 sec. Phase Unbalance; within 8 sec. Phase Reversal; 0.1~0.3 sec. Locked Rotor; Lock : within 0.5sec after D-time(in DEF set) Stall : 0.05 ~ 10sec (in DEF set).. |
| Current Range; Over Current; 0.5~960A(Over 60A with External CTs). Under Current; 0.5~59A/OFF(Over 60A with External CTs). Phase Unbalance; 5~50%. Alert Setting; 50~100% of Oc setting. Time Setting Range; Start Delay Time (D-TIME); 1~200sec (Definitive). Trip Delay Time Setting (O-TIME); INV; 1-30. DEF; 0.2-30 sec. Control Voltage; 110VAC±15%, 220VAC±15%, 24VAC/DC. Output Relay; OC/UC; 2-SPST, 3A/250VAC Resistive. AL/UC; 1-SPST,3A/250VAC Resistive. Time Characteristic; In/"tc"mode; Inverse. dE/"tc"mode; Definite. Trobleshooting/Trip Indication; LED Display(3 Trip causes memory). Current Sensing; 3-CT. Mounting; 35mm DIN-Rail/Panel.. |
| EOCR-3DE. EOCR-FDE... |  |