| EOCR-PMZ. EOCR-PFZ.; ■; MCU( Microprocessor Control Unit )Based. ■; Convenient installation -PMZ:Panel Mounting Type -PFZ:Panel Flush Mounting Type. ■; Full mode function:easy to set. ■; Three Integral Current Transformers. ■; Full cover protection Function. ■; Wide Current Range protection from 0.1A to 3600A by just 1 model. ■; Built-in digital ammeter. ■; Total running time display. ■; Current display like L1 -> L2 -> L3 -> GF.... ■; Bar-Graph monitoring on impending overload trip. ■; Selectable time-current characteristics[Inverse/Inverse based on thermal Memory (Thermal Inverse) /Definite]. ■; 4~20mA current loop communcations. ■; Test Function. ■; Operates in wide ambient temperature range. ■; Selectable Fail-safe Operation/ No volt Release(FS:ON).. |
| --- |
| Protective Item; Trip Time. Over-current; DEF:0.2~30 sec, INV:1~30 class. Under-current; 0.5~30 sec. Phase Reversal; 0.1~0.3 sec. Phase Unbalance; within 8 sec. Ground Fault; DEF:0.1~10 sec, INV:1~10 class. Locked Rotor; 0.5 sec after d-time. stall; 0.05~10 sec.. |
| Current Setting Range; Over-Current(oc); 0.1~3600A(Over 60A with External CTs). Under-Current(uc); OFF/0.5~less than "OC" setting. Ground Fault Current(Ec); OFF. 0.3~10A:definite. 0.3~1A definite/inverse (selectable). Time Setting; Starting Delay Time(dt); OFF~200sec. Over-Current Trip Time(ot); Definite Time; 0.2~30sec. Inverse Time; 1~30class(30curves). Under-Current Trip Time(ut); 0.5~30sec, definite time characteristics, if "uc" mode selects OFF, then ut is automatically disabled.. Ground Fault Trip Time(Et); Definite/Inverse : 0.05, 0.1~1~10 sec. Ground Failt Starting Time(Edt); OFF/1~10 sec. Tolerance; Current; ±5%. Time; ±5%. Conrol Power; 220; 85~250VAC/DC, 50/60Hz. Output Relay; OL(SH); 2-SPST; 3A/250VAC, Resistive. GR; 1-SPST; 3A/250VAC, Resistive. Environment; Temperature; Store; -30 ~80 ℃. Operation; -20 ~60 ℃. Humidity; 30~85% RH, Non-Condensing. Display; 7-Segment LEDs; 3phase current,Trip cause, Operating hour. Bar-Graph; Load factor for current setting(50~100%). Insulation; Between casing and circuit:over 10MΩ, 500VDC. Dielectric Strength; Between casing and circuit; Between casing and circuit 2000VAC,60Hz, 1min. Between open contacts; Between open contacts 1000VAC, 60Hz, 1min. Between circuit; Between circuit 2000VAC,60Hz, 1min. Electrostatic Discharge; IEC61000-4-2; Lever3:Air Discharge:±8kV, Contact Discharge:±6kV. Radiated Electromagnetic Field Disturbance; IEC61000-4-3; Lever3:10V/m,150MHz&450MHz Portable transceiver. EFT/Burst; IEC61000-4-4; Lever3:±2kV, 1min. Surge; IEC61000-4-5; Lever3:1 x 50 ,±4kV(0˚,90˚,180˚,270˚). 1MHz Burst disturbance; IEC61000-4-12; Lever3:±2.5kV,1MHz. Conducted Emission; EN55011; Class B.. |
| EOCR-PMZ. EOCR-PFZ... |  |